## Sheet1
Calculating Pressure Loss - Equivalent Pipe Length Method
Project: |  | Example |  | Note!
Date: |  | xxxxxx |  | Adapt to the flow and pressure loss units to the data available for your system
Piping Material: |  | PVC Schedule 40 |  | Equivalent Length of Component
Pressure Loss
Imperial Units
Section | Pipe Size (inches) | Flow (gal/min) | Pressure Loss (ft/100ft) | System Components | Equivalent Length of Component (ft) | No. Components | Equivalent Length (ft) | Section Pressure Loss (ftH20) | Total Pressure Loss - Path 1 (ftH2O) | Total Pressure Loss - Path 2 (ftH2O)
1 |  |  |  | 90 deg Elbows | 2.7 | 2 | 5.4
|  |  |  | 45 deg Elbows | 1.3 | 4 | 5.2
0
0
|  |  |  | Straight Pipe | 1 | 20 | 20
SUM 1 | 1 | 10 | 9.6 |  |  |  | 30.6 | 2.9376 | 2.9376 | 2.9376
2 |  |  |  | Tee | 2.4 | 2 | 4.8
|  |  |  | 90 deg Elbows | 2.3 | 4 | 9.2
0
0
|  |  |  | Straight Pipe | 1 | 12 | 12
SUM 2 | 3/4 | 8 | 15 |  |  |  | 26 | 3.9 | 3.9
3 |  |  |  | 90 deg Elbows | 2.7 | 2 | 5.4
|  |  |  | 45 deg Elbows | 1.3 | 4 | 5.2
0
0
|  |  |  | Straight Pipe | 1 | 10 | 10
SUM 3 | 1 | 10 | 9.6 |  |  |  | 20.6 | 1.9776 | 1.9776 | 1.9776
4 |  |  |  | Tee | 1.7 | 2 | 3.4
|  |  |  | 90 deg Elbows | 2.2 | 4 | 8.8
0
|  |  |  | Balanc. Valve | 24 | 1 | 24
|  |  |  | Straight Pipe | 1 | 12 | 12
SUM 4 | 1/2 | 2 | 8 |  |  |  | 48.2 | 3.856 |  | 3.856
Total SUM | [8 empty] | 8.8152 | 8.7712
SI Units
Section | Pipe Size (DN) | Flow (litre/sec) | Pressure Loss (mm/100m) | System Components | Equivalent Length of Component (m) | No. Components | Equivalent Length (m) | Section Pressure Loss (mmH20) | Total Pressure Loss - Path 1 (mmH2O) | Total Pressure Loss - Path 2 (mmH2O)
1 |  |  |  | 90 deg Elbows | 0.8 | 2 | 1.6
|  |  |  | 45 deg Elbows | 0.4 | 4 | 1.6
0
0
|  |  |  | Straight Pipe | 1 | 20 | 20
SUM 1 | 25 | 0.6 | 6000 |  |  |  | 23.2 | 1392 | 1392 | 1392
2 |  |  |  | Tee | 0.7 | 2 | 1.4
|  |  |  | 90 deg Elbows | 0.7 | 4 | 2.8
0
0
|  |  |  | Straight Pipe | 1 | 12 | 12
SUM 2 | 20 | 0.3 | 5800 |  |  |  | 16.2 | 939.6 | 939.6
3 |  |  |  | 90 deg Elbows | 0.8 | 2 | 1.6
|  |  |  | 45 deg Elbows | 0.4 | 4 | 1.6
0
0
|  |  |  | Straight Pipe | 1 | 10 | 10
SUM 3 | 25 | 0.6 | 6000 |  |  |  | 13.2 | 792 | 792 | 792
4 |  |  |  | Tee | 1.3 | 2 | 2.6
|  |  |  | 90 deg Elbows | 0.7 | 4 | 2.8
0
|  |  |  | Balanc. Valve | 1 | 1 | 1
|  |  |  | Straight Pipe | 1 | 12 | 12
SUM 4 | 15 | 0.13 | 5100 |  |  |  | 18.4 | 938.4 |  | 938.4
Total SUM | [8 empty] | 3123.6 | 3122.4